INTERNATIONAL WORKSHOP ON LEVEL 2 PSA AND SEVERE ACCIDENT MANAGEMENT

:

“EXPERIENCE GAINED FROM THE MEXICAN NUCLEAR REGULATORY AUTHORITY IN THE PROBABILISTIC SAFETY ASSESSMENT  LEVEL 2 DEVELOPMENT FOR LAGUNA VERDE NUCLEAR POWER PLANT”

Verónica Godínez S. and  Ramón López M.

Comisión Nacional de Seguridad Nuclear y Salvaguardias

Dr. Barragán 779, Col. Narvarte, 03020 México D.F.

Phone (52) 55 50 95 32 41, Fax (52) 55 55 90 61 03

E-mail: vgodinez@cnsns.gob.mx

## ABSTRACT

The Mexican Nuclear Regulatory Authority has developed their own Probabilistic Safety Assessment Level 2 in order to have an independent model to evaluate PSA application as well as to compare the main results of the Individual Plant Examination (IPE) review process. The scope of the study considers internal events and it was developed using the methodology described in the NUREG-1150. Therefore, based on the results obtained in the PSA level 1, an Accident Progression Events Tree was developed taking into account the phenomenology and systems dependencies that could occur during the evolution of a severe accident in the Laguna Verde NPP. An analysis of the dominant pathways for each Plant Damage State (PDS) was developed according to the failure modes of the primary containment, as well as the fission products released to the environment and their related parameters. A radioactive release characterization and conditional failure probability of the containment for each release pathway was obtained. MELCOR code was used to simulate the evolution of selected severe accident sequences and a plant specific XSOR type of code was developed to estimate the source term. In this paper the PSA level 2 results are presented, as well as the experience gained and their applications to the IPE review process.

- Introduction

The Laguna Verde NPP has two Boiling Water Reactors (BWR/5), designed and supplied by General Electric within a MARK II containment. The unit one began its commercial operation in 1990 and unit two followed in 1995. In order to mitigate severe accidents, there are several systems that supply coolant injection to the core. Two systems provide coolant to the core at high pressure: the High Pressure Core Spray system (HPCS), and the Reactor Core Isolation Cooling system (RCIC). For low pressure  scenarios, the Low Pressure Core Spray (LPCS) and the Low Pressure Core Injection system (LPCI) can supply coolant to the core. The Automatic Depressurization System (ADS) is used to reduce the vessel pressure using five safety relief valves conducting steam to the suppression pool. The Main Feedwater System (FW) and the Condensate System (CDS) are used as primary sources of water.  In case of loss of offsite power, three diesel generators can supply emergency AC power.

The containment design employs a steel line reinforced concrete structure utilizing the over-and-under pressure suppression concept, which consist of a drywell over a pressure suppression chamber. Containment sprays are located in the containment to condense steam and suppress the pressure and temperature. Containment can be vented if the pressure cannot be suppressed by the RHR system. To reduce the potential of hydrogen combustion, the containment is inertized with nitrogen.

The internal design pressure of the primary containment is 45 psig. The ultimate containment failure pressure assessed with a containment structural analysis is 165 psig. Several containment failure locations were identified, for instance the drywell head, the suppression pool floor union with the wetwell wall, among others. The nominal free volumes of the drywell and the suppression chamber are 4357 m3  and 3170 m3 respectively. The nominal volume of the suppression pool is 3166 m3. The ratio between the thermal power and the containment volume, which relates with the containment loads capacity is 0.19 MWt/m3. The vent pipe ties into the standby gas treatment system (SGTS). The operators are instructed to vent the containment when the containment pressure exceeds 60 psig.

As part of the licensee base, the Mexican Nuclear Regulatory Authority (CNSNS) requested the utility to perform an Individual Plant Examination (IPE). In parallel, the CNSNS began to develop their own Probabilistic Safety Assessment Level 1 and 2 in order to have an independent model to evaluate PSA application as well as to get experience and means to compare  the LVNPP IPE as part of the review process. The NSAC-159 methodology was selected for the Mexican utility to perform the back-end portion of the IPE and the CNSNS make used of the NUREG-1150 methodology to perform their own level 2 probabilistic model.

### Level 2 PSA Methodologies

The accident progression assessment methodologies has progressed from the simple containment event trees (CET) used in the WASH-1400 study, to the more complex Accident Progression Event Tree (APET), with a complete uncertainty analysis, used in the NUREG-1150.

The containment event tree, also called accident progression event tree, provides a structured approach for systematic evaluation of the containment capability to cope with severe accidents. The CET is used to characterize the progression of a severe accident and to identify containment failures modes that could lead to fission product release. There are two main methodologies employed for the development of the CETs: the large CET method, which contains, in detailed, as  top event questions all the events and phenomena that influence the evolution of a severe accident; and the small CET method, similar to those used in the level 1 PSA, which includes top event questions concerning the major severe accident phenomena, supported by fault trees.

The quantification of the branch probabilities takes into account calculations and analyses using mechanistic computer codes, parametric codes and engineering judgment (especially for phenomenological questions), as well as systems analysis for questions related with systems availability. The differences in the above methods do not diminish the quality of the results as long as the important features that influence the evolution of the accident are treated in detailed, and the dependencies between questions are properly handled.

- CETs developed for LVNPP.

  - Utility

The small CET method was selected by the utility to develop the Level 2 of the IPE. Nine Plant Damage States (PDS) were defined by binning the Level 1 PSA end states and assessed in equal number of CETs developed for the accident progression analysis. The CET top head includes: the status of the vessel pressure, the coolant recovery, the vessel failure modes, the early and late containment failure, the early and late suppression pool scrubbing, the core concrete interaction and the fission product retention. The main phenomenological aspect such as in and ex-vessel steam explosion, direct containment heating (DCH), high pressure melt ejection (HPME), system availability and human error were modeled by means of approximately 160 fault tree models. The  accident progression paths obtained for every CET, range from 50 to 400. The quantification process was performed by means of the CAFTA computer code and the MAAP code was used to support the development of the CET´s.

  - CNSNS

The NUREG-1150 methodology was used by the Regulatory Authority to perform their own level 2 PSA. Therefore, an APET of 131 questions was developed to assess the 25 PDS obtained from the CNSNS level 1 PSA.  More than 1000 accident progression paths were identified from the APET. The questions included in the APET cover the main phenomenological aspect along with systems availability and operator actions. The APET covers conditions before core damage (initiating event, vessel pressure, emergency systems conditions etc), containment conditions after and before vessel failure, mitigation systems availability,  and phenomenology aspect such as hydrogen production, oxidation of zircalloy, core-concrete interaction, in-vessel and ex-vessel steam explosions. Containment failures modes such as rupture, leak or venting as well as their location were assessed in the APET for the different accident progression time frames. Examples of the APET questions are: Amount of the zirconium oxidized in the vessel pressure?, Is the molten material coolable?, What is the location of the primary containment failure?. The quantification process was performed by means of the EVNTRE computer code developed by Sandia National Laboratories and the MELCOR code was used to support the APET development.

A parametric computer code called LVSOR, which is based on the XSOR type of codes, was developed for the source term estimation. LVSOR employs a parametric equation based on mass conservation that takes into account the phenomenon and events related with the accident progression. Every parameter represent either a release or a decontamination factor and their figures are estimated based on MELCOR simulations.

A criteria based on the fraction of iodine and cesium released to the environment was used to assign each source term into a release category. The criteria takes into account the initial core inventory and the time at which the release begins. The source terms were classified in nine categories, according to the time of release: early (less than 6 hrs), intermediate (from 6 to 24 hrs) and late (more than 24 hrs), and the amount of radioactive material released: high, medium and low. The high release category was defined when more than 10% of Cs-I or an equivalent amount of radioactive material is released and capable to cause early deads. The medium release category can cause health effect in the medium or short time with a release of 1 to 10% of Cs-I while the low category is responsible of latent health effects with release of less than 1% of Cs-I.

- Level 2 Results

The figure 1, shows the containment failure modes for different accident scenarios. The CNSNS study shows that the conditional probability of early containment failure is 0.36 compared with the 0.15 in the IPE. The late conditional probability of containment failure is 0.42 compared with the 0.66 of the IPE. The conditional probability of no containment failure estimated in the CNSNS study is 0.07 compared with the 0.19 of the IPE. The opening of the main steam isolation valves (MSIV´s) for venting the reactor vessel during primary containment flooding scenarios which was not considered in the CNSNS study as well as other conservatisms were identified as the main contributors for the higher early containment failure probability and less no containment failure probability obtained in the regulatory assessment.

The conditional probability of radioactive release outside the reactor building in the intermediate period is 0.7 in the CNSNS study compared with the 0.67 estimated by the utility IPE. The late period follows with 0.16 in the CNSNS study compared with the 0.9 in the IPE. The CNSNS estimation for the early period is 0.07 compared with the 0.05 in the IPE, and the major difference is in the case of no release with 0.07 in the CNSNS assessment compared with the 0.19 in the utility study.

Both studies show similar results for the of radioactive material released in each period of time, however there are differences in the intermediate period. The regulatory model estimates a conditional probability of high release, within this period of time, of 0.83 compared with the 0.43 obtained in the IPE. A high release in late period is estimated in the CNSNS study with a conditional probability of 0.99 compared with the 0.82 in the IPE. For a release of high magnitude in the early period the CNSNS estimates a conditional probability of 0.02 compared with the 0.1 in the IPE.

The largest source terms in both studies are associated with the Station Blackout scenarios. The overpressure is the dominant containment failure mode with a conditional probability of 0.37 in the utility study and 0.45 in the CNSNS assessment. The dominant failure location is in the drywell. The bypass of the primary containment was modeled only in the utility study. The containment bypass occurs when the main steam isolation valves (MSIV) are opened during containment flooding following the emergency operating procedures.

- Experience Gained in the Review process

The experience gained during the development of the regulatory PSA allow us to focus the review process was on those important features of the EPRI methodology, such as:

Timing of phenomenological issues. The occurrence of some phenomena are related with the early or late containment failure or with the vessel breach. Therefore the event tree headings and/or the fault trees should adequate represent those time relationships.  Moreover it was identified the timing of containment failure, which can occur before, after or at the time of core damage and/or vessel breach The event and fault trees were reviewed to assure that the key phenomena and processes of the severe accident progression were identified. Also, the fault trees development for each top heading was considered another important task, and consequently it was reviewed in detail. The review was focused on the consistency of the system models and the phenomenological timing. The review of the fault tree models indicate that it was necessary to consider more than one figure for some important parameters like the fraction of core melt depending on the conditions of sequences considered, in order to assess the impact of this parameter in the accident progression paths. However, the definition of the potential figures of this parameter is not an easy task due to the uncertainty of this phenomena. For example, the revision of the MAAP code used considers that once the 20% of the core has been melted and relocated, the vessel failure can not be avoided. Also the vessel failure,  according to MAAP, can not be avoided if the injection  is restored once the code predicts the blockage conditions in the fuel channels. The first example  suggests that only two scenarios might be considered, when more than 20% of core is melted and the other when less than 20%.  In the second example it is highly uncertain the definition of the blockage conditions. The NUREG 1150 methodology considers these aspects by means of the uncertainty analysis of the different physical combinations of these parameters. Therefore, these methodological aspects were discussed between the regulatory and utility staffs.

Parameters figures. Consideration of important parameters which are highly unknown may conduce to different results. So special emphasis during the review was paid to parameters describing the amount of the core melt, the steam generated in a steam explosion, etc. It was necessary to review also the treatment of the dependencies among phenomenon. For example enough water on the cavity should exist to produce an ex-vessel steam explosion, so the review makes sure that the required events or conditions that should have previously occurred were included in the analysis. Based on the experience acquired during the development of the own PSA, it was also reviewed the methods used to estimate probabilities of plant specific events as well as the methods used to quantify the event trees.

The usage of simulation code results. Some severe accident sequences, basically the dominants ones like the Station Blackout, were reproduced with the MAAP code in order to obtain parameters which characterize the accident sequences.

- Containment structural analysis. The utility used the ANACAP (the ANATECH Concrete Analysis Package) finite element computer code to determine the ultimate containment capacity. Based on the importance of the ultimate containment failure pressure on the source term release during a severe accident the regulatory body reviewed in detail the containment structural analysis and its quantification.

The source term analysis. This task was reviewed once the previous task modifications or improvements were implemented. The strategy was to review the source term analysis with a comparative assessment of the utility approach and the regulatory own PSA methodology. The regulatory PSA uses a parametric model with data obtained from severe accident codes to estimate the source term releases. The parametric model corresponds to the XSOR type of codes, which are capable to estimate thousand of source terms based on a parametric equation.

The results of review process included modifications and improvements of the CET structure and fault tree models as well as improvements on the input deck of MAAP. For instance, the relationship between the primary containment failures modes and their locations were implemented and the fault tree for the vessel failure modes was expanded to cover all failures modes such as thermal attack, steam explosion at high and low pressure as well as the ALPHA mode.

- CONCLUSIONS

The PSA experience of the regulatory authority justifies the detailed review approach used and provides the required background for the comparative assessment of the methodologies used (NSAC/159 and NUREG-1150). In general, both studies show similar trends in the accident progression features and the source term released. The figures obtained from the regulatory study were used as the base to perform qualitative comparison and to obtain trends instead of an exact quantitative comparison. The IPE review and its comparison with the CNSNS model confirm that in principal, neither method is more complete. The small CET method is more traceable, and considerably easier to review. However, one important aspect of the PSA level 2 development is the treatment of the uncertainties, the IPE for Laguna Verde did not characterize this uncertainties, and therefore the regulatory authority is planning to complete their own Level 2 assessment with an uncertainty analysis like the one performed in the NUREG-1150.

| CONTAINMENT FAILURE MODE | ATWS (9.03E-6) | LOCA ( 8.66E-07) | SBO ( 6.95E-05) | T-LOCA ( 7.22E-06) | TRANS (2.43E-06) | ALL (9.03E-05)* |
| --- | --- | --- | --- | --- | --- | --- |
| Containment failure before vessel breach. The vessel breach occurs at high pressure. | 0.9 % |  | 37% |  | 8.7% | 0.4% |
| Containment failure before vessel breach. The vessel breach occurs at low pressure. | 0.1% | 90% |  | 55.7% | 78 % | 36% |
| Containment failure at/near the vessel breach. | 7% | 10 % | 15% | 14% | 13% | 14% |
| Containment failure after vessel breach. | 92% |  | 40% | 20.6% |  | 42% |
| There is not release to the environment. |  |  | 7.5% | 9.6% |  | 7% |

Figure 1. CNSNS Accident Sequences Analysis and Containment Failure Modes

* CDF